## Sheet1
WORTHAM THEATER
NEW BAS POINT LIST
VERSION DATE: 4-15-14
GENERAL
ALL EQUIPMENT SHALL HAVE START/STOP CONTROL , STATUS INDICATION (ON/ OFF/ IN ALARM), LOGGED CUMULATIVE RUN TIME
ALL SETPOINTS (TEMPERATURE, PRESSURE) SHALL BE DISPLAYED AND ADJUSTABLE VIA THE BAS
SEE SCHEDULES FROM ORIGINAL INSTALLATION FOR COIL GPMS
AIR HANDLERS
NOTE: ALL EXISTING VALVE AND DAMPER OPERATORS ARE PNEUMATIC (AND NEED TO BE CHANGED) UNLESS NOTED AS 'DDC'
UNIT /SERVES/ TYPE | LOCATION | Single zone H/C | Multi-zone (1 actuator per zone) | Re-heat valve/actuator | Hot water valve/actuator | Cold water valve/actuator | Motor HP & Frame | Zone sensors | Hot deck sensor | Cold deck sensor | Discharge Air Temp sensors | Return Air Temp sensors | RAT sensors w/Co2 | Outside Air Damper Actuator | Return Air damper Actuator | Freeze Stat | OAT/Humidity sensor | Existing VFD | Add VFD as part of this project
BASEMENT
B-1 Musicians, Dressing, etc. |  |  | 6 | 3 |  | 1 | 15 / 254T | 6 |  | 1 | 3 | 1 | [6 empty] | YES
Multi-Zone
B-2 Cullen Orch Pit & Traps |  | Y |  |  | 1 | 1 | 2 / 145T | 1 |  | 1 | 1 |  | 1 | 1
Single Zone
B-3 Cullen Orch Lift Equip Rm | [5 empty] | 1 |  | 1 |  |  | 1
FCU ( no heat) |  |  | Fan to start when calling for cooling
B-4 Brow Orch Pit |  | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  | 1
Single Zone |  |  |  |  | DDC | DDC
B-5 Brown Orch Pit Equip Rm | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
B-6 Air Comp. & Wagon lift Rm | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
B-7 BT Orch LvL Seating |  | Y |  | 1 | 1 | 1 | 40 / 326T TE | 2 |  | 1 | 2 | 1 | [6 empty] | YES
Single Zone
B-8 BT Grand Tier LvL seating | [5 empty] | 1 | 15 / 254T | 1 |  |  | 1 | 1 | [6 empty] | YES
Single Zone
B-9 CT Orch LvL Seating |  | Y |  | 1 | 1 | 1 | 20 / 256T | 2 |  | 1 | 2 | 1 | [6 empty] | YES
Single Zone
B-10 BT Inst. Storage (not used) |  |  |  | 1 |  | 1 | 1.5 / 145T | 1 |  | 1 | 1 | 1
Single Zone with Humidifier |  | Zone temp/humidity sensor
Note: Owner to Replace humidifier
B-11 CT Inst. Storage (not used) |  |  |  | 1 |  | 1 | 2 hp? | 1 |  | 1 | 1 | 1
Single Zone with Humidifier |  | Zone temp/humidity sensor
Note: Owner to Replace humidifier
B-12 HGO wardrobe & Dressing |  |  | 10 | 4 |  | 1 |  | 10 |  | 1 | 4 |  | 1 | 1
Multi-Zone | [6 empty] | Add OA actuator missing from original construction
B-13 Ballet Wardrobe & Dressing |  |  | 4 |  |  | 1 | 10 / 215T | 4 |  | 1 |  |  | 1 | 1 |  |  |  |  | YES
Multi-Zone
B-14 CT Orch Light, Sound Rm & Etc. |  |  | 5 | 4 |  | 1 | 7.5 / 213T | 5 |  | 1 | 4 |  | 1 | 1
Multi-Zone
B-15 Dressing Rms. Etc. |  |  | 4 | 2 |  | 1 | 5 / 184T | 4 |  | 1 | 2 |  | 1 | 1
Multi-Zone
B-16 FOH Bsmt & Tunnel |  | Y |  |  | 1 | 1 | 7.5 hp | 1 |  | 1 | 1 | 1
Single Zone
B-17 Wig & Visitors Wardrobe | [5 empty] | 1 | 3 hp? | 1 |  |  | 1 | 1
FCU
B-18 BT Traps |  | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1
Single Zone
B-TR |  | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 | [6 empty] | I
Single Zone |  |  |  |  | DDC | DDC
IST FLOOR
1-1 Prairie Lobby | 1st floor mech rm | Y |  | 1 | 1 | 1 | 15 / 254 | 2 |  | 1 | 2 | 1 | [6 empty] | YES
Single Zone
1-2 BT Control Rms. | 1st floor mech rm |  | 5 | 4 |  | 1 | 3 / 182T | 5 |  | 1 | 9 | 1 | 1
Multi-Zone
1-3 HL&P | 1st floor mech rm | Y |  | 1 |  | 1 |  | 1 |  |  | 2 | 1
Single Zone
2ND FLOOR
2-1 Bmst Rehearsal | 1st floor mech rm | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
2-2 Security |  | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
FCU | [6 empty] | Unit also has an electric reheat coil to be controlled
(Not currently on BAS- add as part of this Project )
2-3 WCOC Offices | 2nd floor mech rm |  |  | 1 |  | 1 |  | 1 |  |  | 2 |  | 1 | 1
Single Zone
2-4 Texas Lobby | 2nd floor mech rm | Y |  |  | 1 | 1 | 25 / 286TE | 1 |  | 1 | 1 | 1 | [6 empty] | YES
Single Zone
2-5 Ticket Office | 2nd floor mech rm |  | 3 | 1 |  | 1 | 5 hp | 3 |  | 1 | 4 | 1
Multi-Zone
2-6 Dimmer/Elect Rm. | 2nd floor mech rm | Y |  |  | 1 | 1 | 15 / 254T | 1 |  | 1 | 1 | 1 | [6 empty] | YES
Single Zone
3RD FLOOR
3-1 2nd/3rd fl East | 3rd floor mech rm |  | 6 | 4 |  | 1 | 7.5 / 213T | 6 |  | 1 | 4 |  | 1 | 1
Multi-Zone
3-2 Green Room | 3rd floor mech rm |  | 4 | 1 |  | 1 | 7.5 / 213T | 4 |  | 1 | 1 |  | 1 | 1
Multi-Zone
3-3 Locker Rms | 3rd floor mech rm |  |  | 2 |  | 1 | 5 / 184T | 3 |  |  | 3 |  | 1 | 1
Single Zone
3-4 Brown Stage Rear | 3rd floor mech rm | Y |  |  | 1 | 1 | 15 / 254T | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  |  | YES
single Zone
3-5 BT Far Stage Rt. | 3rd floor mech rm | Y |  |  | 1 | 1 | 15 / 254T | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  |  | YES
Single Zone
3-6 Green Rm Elevator Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
4TH FLOOR
4-1 N/E Offices | Mech 438 |  | 4 | 2 |  | 1 | 7.5 / 213T | 4 |  | 1 | 2 |  | 1 | 1
Multi-Zone
4-1A HGO IT Office | Mech 438 | Y |  |  | 1 | 1 |  | 1 |  |  | 1 | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
4-2 HFC Offices | Mech 421 |  | 5 | 2 |  | 1 | 7.5 / 213T | 5 |  | 1 | 2 |  | 1 | 1
Multi-Zone
4-2A HFC Conf Rm | Mech 421 | Y |  |  | 1 | 1 |  | 1 |  |  | 1 | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
4-3 GF Hallways |  |  | 3 |  | 1 | 1 | 25 / 284T DP | 3 | 1 | 1 | 3 | 1 | [6 empty] | YES
Multi-Zone
4-4 Founders Salon | Mech 443 |  |  | 1 |  | 1 | 10 / 215 | 2 |  | 1 | 1 |  | 1 | 1
Single Zone | [18 empty] | YES
4-5 BT Stage Lt. | Mech 443 | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1
Single Zone
4-6 HGO Server Rm | ELEC 439 |  |  |  |  | 1 |  | 1 |  |  | 1
Single Zone
5TH FLOOR
5-1 ELEV MACH ROOM
not on new BAS
5-2 3rd Fl Rehearsal | MECH 501 | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
5-4 4th/5th Floors | MECH 510 |  | 4 | 1 |  | 1 | 7.5 / 213T | 4 |  | 1 | 1 |  | 1 | 1
Texas Multi-Zone
5-5 HGO Offices North |  |  | 4 | 2 |  | 1 | 7.5 / 213T | 4 |  | 1 | 2 |  | 1 | 1
Multi Zone
5-6 BT Stage Rt. | Mech 510 | Y |  |  |  | 1 | 15 / 254T | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  |  | YES
Single Zone
5-8 5 FOH Hallways | mech 548 |  | 5 |  | 1 | 1 | 20 / 256 | 4 | 1 | 1 | 4 | 1 | [6 empty] | YES
Multi-Zone | [6 empty] | CONFIRM
5-9 GF/Tex S.W. Stairs |  | Y |  |  |  | 1 | 25 / 284T TE | 1 |  |  | 1 | 1 | [6 empty] | YES
Single Zone
5-10 Cullen Alcove |  | Y |  |  | 1 | 1 | 5 / 184T | 1 |  | 1 | 1 | 1
Single Zone
6TH FLOOR
6-1 Cullen Dimmer/Spot |  |  | 2 | 2 |  | 1 | 7.5 / 213T | 2 |  | 1 | 2 | 1 |  |  |  | 1
Multi-Zone
6-2 4th Fl Rehearsal | MECH 630 | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
6-3 CT Mezzanine | MECH 630 | Y |  |  | 1 | 1 | 20 / 256T | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  |  | YES
Single Zone | [6 empty] | Has roof top pressure release (F-25)
6-4 Cullen Stage | MECH 630 | Y |  |  | 1 | 1 | 20 / 256T | 1 | 1 |  | 1 | 1 |  |  |  | 1 |  |  | YES
Single Zone
6-7 7th Fl Elect/Mech | [5 empty] | 1 | 1.5/145T-85 | 1 |  |  | 1 | 1
Single Zone
6-8 6th Fl HGO North |  |  | 4 | 4 |  | 1 |  | 4 |  | 1 | 4 |  | 1 | 1
Multi-Zone
6-11 GF/Tex S.E. Stairs |  | Y |  |  | 1 | 1 | 25 HP | 1 |  | 1 | 1 |  | 1 | 1 |  | 1 |  |  | YES
Single Zone
6-12 Brown Alcove |  | Y |  |  | 1 | 1 | 5 HP | 1 |  | 1 | 1 |  | 1 | 1 |  | 1
Single Zone
6-13 Grand Foyer |  | Y |  |  | 1 | 1 | 40 / 326TE | 1 |  | 1 | 1 |  | 1 | 2 | 1 | 1 |  |  | YES
Single Zone | [6 empty] | Has roof top pressure release (F-24)
6-14 Texas Elevator Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
6-15 CP Elevator Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
6-16 Central Plant Office |  | Y |  |  | 1 | 1 |  | 1 |  |  | 1
FCU
6-17 HGO Office & Lobby | MECH 606 |  | 3 | 3 |  | 1 | 7.5 / 213T | 3 |  | 1 | 3 |  | 1 | 1 |  | 1
Multi-Zone
6TH FLOOR
7-1 BT Control Rms. | MECH 745 |  | 4 | 4 |  | 1 | 10 HP | 4 |  | 1 | 4 | 1 | [6 empty] | YES
Multi-Zone
7-2 BT Balcony | MECH 744 | Y |  |  | 1 | 1 | 15 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1 |  | YES
Single Zone | [7 empty] | w/Bell & Gossett pump HW by pass loop & 1-HW loop sensor
Has roof top pressure release (F-26) w/actuator just upstream of AHU
7-3 5th/6th Fl HGO East | MECH 744 |  | 6 | 3 |  | 1 | 15 / 254T | 6 |  | 1 | 3 |  | 1 | 1 |  | 1 |  |  | YES
Multi-Zone
7-4 Brown Dimmer/Elect | MECH 744 | Y |  |  | 1 | 1 | 7.5 / 213T | 1 |  | 1 | 1 | 1
Single Zone
7-5 Brown Grid | CORRIDOR |  |  |  |  | 1 | 5 / 184T | 1 |  |  | 1 | 1
Single Zone
7-6 Outside AHU | MECH 741 | Y |  |  | 1 | 1 | 15 HP |  | 1 |  | 1 |  |  | 1 |  | 1 | 1 |  | YES
Single Zone | [7 empty] | w/Bell & Gossett pump HW by pass loop & 1-HW loop sensor
1 - Discharge/Supply Air Actuator
7-7 Actors Elevator Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
7-8 West Prairie Elev Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
7-9 East Prairie Elev Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
7-10 6 FOH Hallways |  |  | 4 |  | 1 | 1 | 25 / 284 | 4 | 1 | 1 | 4 |  | 1 | 1 |  | 1 |  |  | YES
Multi-Zone
7-12 Sm Freight Elev Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
7-13 Lg Freight Elev Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU |  |  | Fan to start when calling for cooling
7-14 Gockley Rehearsal | MECH 700 | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
7-15 Floyd Rehearsal | MECH 700 | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 | 1 |  |  |  | 1
Single Zone |  |  |  |  | DDC | DDC
(already upgraded & on BACnet)
7-16 Outside AHU |  | Y |  |  | 1 | 1 | 25 HP |  | 1 |  | 1 |  |  | 2 |  | 1 | 1 |  | YES
Single Zone | [7 empty] | w/Bell & Gossett pump HW by pass loop & 1-HW loop sensor
1 - Discharge/Supply Air Actuator
7-17 Security Elevator Rm. | [5 empty] | 1 |  | 1 |  |  | 1
FCU
7-18 Main Electrical Rm. |  | Y |  |  | 1 | 1 |  | 1 |  | 1 | 1 | 1 |  |  |  | 1
Single Zone
7-19 Electrical Rm. & Hallway |  |  |  | 1 |  | 1 | 3 / 182T | 2 |  |  | 1 | 1
Single Zone
Total Count |  |  | 95 | 57 | 36 | 80 |  | 158 | 8 | 50 | 131 | 29 | 34 | 37 | 1 | 13 | 3 | 4
FANS | Location
EF-1 | Roof | Start/Stop /Status (air flow switch)
EF-2 | Roof | Start/Stop /Status (air flow switch)
EF-3 | Roof | Start/Stop /Status (air flow switch)
EF-4 | Roof | Start/Stop /Status (air flow switch)
EF-5 | Roof | Start/Stop /Status (air flow switch)
EF-6 | Roof | Start/Stop /Status (air flow switch)
EF-7 | Roof | Start/Stop /Status (air flow switch)
EF-8 | Roof | Start/Stop /Status (air flow switch)
EF-9 | Roof | Start/Stop /Status (air flow switch)
EF-10 | Roof | Start/Stop /Status (air flow switch)
EF-11 | Roof | Start/Stop /Status (air flow switch)
EF-13 | Roof | Start/Stop /Status (air flow switch)
EF-14 | Roof | Start/Stop /Status (air flow switch)
EF-15 | Roof | Start/Stop /Status (air flow switch)
EF-16 | Roof | Start/Stop /Status (air flow switch)
EF-17 | Roof | Start/Stop /Status (air flow switch)
EF-18 | Roof | Start/Stop /Status (air flow switch)
EF-19 | Roof | Start/Stop /Status (air flow switch)
EF-20 | Roof | Start/Stop /Status (air flow switch)
EF-21 | Roof | Start/Stop /Status (air flow switch)
EF-22 | Roof | Start/Stop /Status (air flow switch)
EF-23 | Roof | Start/Stop /Status (air flow switch)
EF-24 | Roof | Start/Stop /Status (air flow switch). This fan provides pressure relief for AHU 6-13 and shall be software interlocked based on AHU OA damper position
EF-25 | Roof | Start/Stop /Status (air flow switch). This fan provides pressure relief for AHU 6-3 and shall be software interlocked based on AHU OA damper position
EF-26 | Roof | Start/Stop /Status (air flow switch). This fan provides pressure relief for AHU 7-2 and shall be software interlocked based on AHU OA damper position
EF-27 | Roof | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-28 | Roof | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-29 | Roof | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-30D | dryer exh into dock | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-31R |  | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-31D | DOCK EXH | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-32 | MECH RM | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-33 | BOILER RM | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
EF-34 | BOILER RM | Start/Stop /Status (air flow switch). NOTE: THIS FAN IS NOT CURRENTLY ON THE BAS AND SHALL BE ADDED
PUMPS
Chilled Water Pump 1 | 50 HP; 460/3 | Status. | [15 empty] | 1
ADD A NEW VFD TO THIS PUMP
Chilled Water Pump 2 | 50 HP; 460/3 | Status. |  | BOILER RM | [13 empty] | 1
ADD A NEW VFD TO THIS PUMP
Chilled Water Pump 3 | 50 HP; 460/3 | Status. | [15 empty] | 1
ADD A NEW VFD TO THIS PUMP
Chilled Water Pump 4 |  | Status. | [15 empty] | 1
existing VFD w/ LON card; add BACnet card
Cond Water Pump 1 | 50 HP; 460/3 | Status. | [15 empty] | 1
ADD A NEW VFD TO THIS PUMP
Cond Water Pump 2 | 50 HP; 460/3 | Status. | [15 empty] | 1
ADD A NEW VFD TO THIS PUMP
Cond Water Pump 3 | 50 HP; 460/3 | Status. | [15 empty] | 1
ADD A NEW VFD TO THIS PUMP
Cond Water Pump 4 |  | Status. | [15 empty] | 1
existing VFD w/ LON card; add BACnet card
Heating Hot Water Pump 1 | 20 HP; 460/3 | Status. No VFD to be added
Heating Hot Water Pump 2 | 20 HP; 460/3 | Status. No VFD to be added
Domestic Hot Water Circ Pump
Sump Pump Seg 1 |  | Motor status; High Water Level Alarm
Sump Pump Seg 2 |  | Motor status; High Water Level Alarm
Sump Pump Seg3 |  | Motor status; High Water Level Alarm
Sewage Ejector Seg 1 |  | Motor status; High Water Level Alarm
Sewage Seg 2 |  | Motor status; High Water Level Alarm
Domestic Water Pumps |  | Status; Low Pressure Alarm
HYDRONIC HEATING BOILERS
Common Hot water piping |  | Supply /Return Temp
Boiler 1 & 2 |  | Boiler Supply/Return Temp; Boiler Pressure
Hot Water Mixing Valve |  | Control (existing actuator is pneumatic and shall be changed to DDC)
DOMESTIC WATER HEATING BOILERS
Domestic Boiler 3 |  | Boiler Temp and Loop supply Temp; Boiler Pressure
COOLING TOWER
Common |  | One Common Normal/Low/High Water level Sensor
Common |  | One by-pass valve and actuator (existing actuator is pneumatic and shall be changed to DDC)
Common |  | water treatment controller alarm
Cooling Tower FAN 1 | 50 HP 460/3; 2 spd | ADD NEW VFD TO EXISTING 2 SPEED MOTOR
Cooling Tower FAN 2 | 50 HP 460/3; 2 spd | ADD NEW VFD TO EXISTING 2 SPEED MOTOR
Cooling Tower FAN 3 | 50 HP 460/3; 2 spd | ADD NEW VFD TO EXISTING 2 SPEED MOTOR
CHILLERS
Common Chilled water piping |  | Supply /Return Temp.
Common Condenser water piping |  | Supply /Return Temp.
Chill Water plant Bypass Valve |  | Supply /Return Temp.
Chiller 1 |  | Chiller Status (on/ off /in alarm); chilled water re-set; condenser water re-set
Chiller 2 |  | One Chilled Water Isolation Valve and Actuator per chiller (existing actuator is pneumatic and shall be changed to DDC)
Chiller 3 |  | One Condenser Water Isolation Valve and Actuator per chiller (existing actuator is pneumatic and shall be changed to DDC)
Control panel data : IN BID ALTERNATE ONLY
Chiller 4 |  | Chiller Status (on/ off /in alarm); chilled water re-set; condenser water re-set
One Chilled Water Isolation Valve and Actuator per chiller
One Condenser Water Isolation Valve and Actuator per chiller
Control panel data : all data currently available; see screen shot. Adapt panel to communicate in BACnet
LIGHTING CONTACTORS
Lighting Contactors |  | Total of 27 lighting contactors controlled ON & OFF, numbered Dock and C10 - C38
SPACE HEATERS
Central Plant: Dock Space Heater |  | space sensor, discharge air sensor, modulate new DDC hw valve
Loading Dock: Space Heater (west) |  | space sensor, discharge air sensor, modulate new DDC hw valve
Loading Dock: Space Heater (east) |  | space sensor, discharge air sensor, modulate new DDC hw valve
Boiler Room Space Heater |  | space sensor, discharge air sensor, modulate new DDC hw valve
NEW VARIABLE FREQUENCY DRIVES
VFD |  | Map frequency, amps, controlling pressure signal and all data available from the drive. Log cumulative kWh consumed over a stipulated and adjustable period
MISCELLANEOUS
Central Plant Supply Air louvers |  | OA damper actuator and space temperature
Central Plant Refrigerant detector |  | alarm status
Fire Alarm System |  | Single point that shows if facility is in FIRE ALARM
Potable Water Tank |  | Normal/Low/High Water Level Alarm (add existing local alarm to BAS)
Emergency Generator |  | current Generator Status( off, on, alarm), run dates and cumulative run time
Buiding pressurization |  | measured between bldg interior and 3 exterior public doors (Texas street entrance; north & south Prairie St entrances )
Outside air dry bulb and humidity
end of list